## REvalue_input_csv
parameter | comment | base | high_cost_coal | coal_55mingen | hydro_low25p | hydro_high25p | nuclear64 | battery15 | battery30 | wind10LC | wind20LC | wind30LC | solar10LC | solar20LC | solar30LC | wind30LC_solar30LC | wind120HH | solar1A | solar90deg | load_modified
scenario_suffix | input | ClcC70m | ChcC70m | ClcC55m | ClcC70mH-25 | ClcC70mH25 | ClcC70mN64 | ClcC70mB15 | ClcC70mB30 | ClcC70mW10lc | ClcC70mW20lc | ClcC70mW30lc | ClcC70mS10lc | ClcC70mS20lc | ClcC70mS30lc | ClcC70mW30lcS30lc | ClcC70mW120 | ClcC70mS1A | ClcC70mS90d | ClcC70mLmod
suggested_scenario_suffix |  | ClcC70m | ChcC70m | ClcC55m | ClcC70mH-25 | ClcC70mH25 | ClcC70mN64 | ClcC70mB15 | ClcC70mB30 | ClcC70mW10lc | ClcC70mW20lc | ClcC70mW30lc | ClcC70mS10lc | ClcC70mS20lc | ClcC70mS30lc | ClcC70mW30lcS30lc | ClcC70mW120 | ClcC70mS1A | ClcC70mS90d | ClcC70mLmod
economic_dispatch_folder_suffix |  | ClcC70m | ChcC70m | ClcC55m | ClcC70mH-25 | ClcC70mH25 | ClcC70mN64 | ClcC70mB15 | ClcC70mB30 | ClcC70m | ClcC70m | ClcC70m | ClcC70m | ClcC70m | ClcC70m | ClcC70m | ClcC70mW120 | ClcC70mS1A | ClcC70mS90d | ClcC70mLmod
new_conventional_capacity_folder_suffix |  | coallc | coalhc | coallc | coallcH-25 | coallcH25 | coallcN64 | coallcB15 | coallcB30 | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallcW120 | coallcS1A | coallcS90d | coallcLmod
net_load_folder_suffix |  | coallc | coalhc | coallc | coallcH-25 | coallcH25 | coallcN64 | coallcB15 | coallcB30 | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallcW120 | coallcS1A | coallcS90d | coallcLmod
REvalue_folder_suffix |  | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W80_S0d | W120_S0d | W80_S1A | W80_S90d | W80_S0d
generator_cost_suffix |  | coallc | coalhc | coallc | coallc | coallc | coallc | coallc | coallc | coallcW10lc | coallcW20lc | coallcW30lc | coallcS10lc | coallcS20lc | coallcS30lc | coallcW30lcS30lc | coallc | coallc | coallc | coallc
coal_cost | low, mid, or high. Low is base. | low | high | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low
coal_cost_suffix |  | Clc | Chc | Clc | Clc | Clc | Clc | Clc | Clc | Clc | Clc | Clc | Clc | Clc | Clc | Clc | Clc | Clc | Clc | Clc
coal_cost_fkey |  | coallc | coalhc | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallc | coallc
coal_min_gen | percentage, 70p is base | 70 | 70 | 55 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
coal_min_gen_suffix |  | C70m | C70m | C55m | C70m | C70m | C70m | C70m | C70m | C70m | C70m | C70m | C70m | C70m | C70m | C70m | C70m | C70m | C70m | C70m
hydro_energy_mod | percentage, 0 is base, pos or neg direction | 0 | 0 | 0 | -25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
hydro_energy_mod_suffix |  |  |  |  | H-25 | H25
nuclear_new_cap | GW. 0 is base. 64 GW is India plan | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
nuclear_new_cap_suffix | [6 empty] | N64
battery_cap_gw | gw capacity. 0 is base | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
battery_cap_gw_suffix | [7 empty] | B15 | B30
battery_cap_gw_fkey |  | bat0 | bat0 | bat0 | bat0 | bat0 | bat0 | bat15 | bat30 | bat0 | bat0 | bat0 | bat0 | bat0 | bat0 | bat0 | bat0 | bat0 | bat0 | bat0
wind_cost | percentage change | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0
wind_cost_direction | low or high | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low
wind_cost_suffix | [9 empty] | wind10LC: W10lc; wind20LC: W20lc; wind30LC: W30lc | W30lc
wind_cost_fkey |  | windLC0 | windLC0 | windLC0 | windLC0 | windLC0 | windLC0 | windLC0 | windLC0 | windLC10 | windLC20 | windLC30 | windLC0 | windLC0 | windLC0 | windLC30 | windLC0 | windLC0 | windLC0 | windLC0
solar_cost | percentage change | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 30 | 30 | 0 | 0 | 0 | 0
solar_cost_direction | low or high | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low | low
solar_cost_suffix | [9 empty] | solar10LC: S10lc; solar20LC: S20lc; solar30LC: S30lc | S30lc
solar_cost_fkey |  | solarLC0 | solarLC0 | solarLC0 | solarLC0 | solarLC0 | solarLC0 | solarLC0 | solarLC0 | solarLC0 | solarLC0 | solarLC0 | solarLC10 | solarLC20 | solarLC30 | solarLC30 | solarLC0 | solarLC0 | solarLC0 | solarLC0
wind_HH | Hub height in meters. 80m is base | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 120 | 80 | 80 | 80
wind_HH_suffix | [16 empty] | W120
wind_HH_fkey |  | W80 | W80 | W80 | W80 | W80 | W80 | W80 | W80 | W80 | W80 | W80 | W80 | W80 | W80 | W80 | W120 | W80 | W80 | W80
solar_orient | degrees to west 0d, 45d, 90d or 1A for 1 axis tracking | 0d | 0d | 0d | 0d | 0d | 0d | 0d | 0d | [6 empty] | 0d | 0d | 1A | 90d | 0d | bar: wind10LC to solar30LC
solar_orient_suffix | [17 empty] | S1A | S90d
solar_orient_fkey |  | S0d | S0d | S0d | S0d | S0d | S0d | S0d | S0d | S0d | S0d | S0d | S0d | S0d | S0d | S0d | S0d | S1A | S90d | S0d
load_year |  | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014
load_year_suffix
load_modifier | "none", "mod", "mod1". | none | none | none | none | none | none | none | none | none | none | none | none | none | none | none | none | none | none | mod
load_modified_suffix | [19 empty] | Lmod
dispatch_horizon | RT or LA. If LA, include days | RT | RT | RT | RT | RT | RT | RT | RT | [6 empty] | RT | RT | RT | RT | RT | bar: wind10LC to solar30LC
LA_days |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
dispatch_time_suffix
Note on A4: Ranjit: For scenarios with different upfront costs like wind, solar, battery, there will be a common econ dispatch suffix.

## Status Runs
| base | high_cost_coal | coal_55mingen
| ClcC70m | ChcC70m | ClcC55m
wind profiles | done
solar profiles | done
net load | done
screening curves | done
economic dispatch

## Screening curves
Screening curves |  |  | INR per USD | 65 | [5 empty] | MAIN COST DATA
|  |  | lbs per kg | 2.2
|  |  | GJ per MMBTU | 1.055 | [6 empty] | Discount Rate | CRF |  | Coal Capital Cost (USD/kW) |  | Coal Fuel Cost (USD/GJ) |  | CT Capital Cost (USD/kW) |  | CCGT Capital Cost (USD/kW) |  | Gas Fuel Cost USD/GJ) |  | Wind Capital Cost (USD/kW) | Wind O&M Cost(USD/kW-y) |  | Solar PV Capital Cost (USD/kW) | Solar O&M Cost (USD/kW-y) |  | Battery Capital Cost (USD/kW) | Battery O&M Cost (USD/kW-y)
|  |  | Btu per kcal | 3.9657 | [5 empty] | discr4 | 4% | 0.064012 | coallc | 976.4278 | coallvc | 2.6154 | ctlc | 678.2677 | ccgtlc | 775.1631 | gaslvc | 3.6923 | base | 1100 | 15 | base | 900 | 10 | base
Fuel cost (Rangan's article) | [9 empty] | discr7 | 7% | 0.085811 | coalhc | 3233.3116 | coalhvc |  | cthc |  | ccgthc |  | gashvc | 10 | W10lc | 990 | 15 | S10lc | 810 | 10 | B20lc
Coal (INR/GJ) | 170 | [8 empty] | discr10 | 10% | 0.11017 | [10 empty] | W20lc | 880 | 15 | S20lc | 720 | 10
Coal (USD/GJ) | 2.6154 | [21 empty] | W30lc | 770 | 15 | S30lc | 630 | 10
Coal Calorific value (kcal/kg) | 3900 | [9 empty] | scenario (generator_cost_suffix)
Coal Calorific value (GJ/tonne) | 16.3176 | [9 empty] | scenario | coallc | coalhc | coallcW30lc | coallcS30lc | coallcW30lcS30lc
Coal (INR/tonne) | 2773.992 | [9 empty] | scenario_coal_gas | coallc | coalhc | coallc | coallc | coallc
Coal (USD/tonne) | 42.6768 | [9 empty] | scenario_wind (blank for base) | base | base | W30lc | base | W30lc
Coal (kg/kWh) computed | 0.57692 | [9 empty] | scenario_solar (blank for base) | base | base | base | S30lc | S30lc
Coal (kg/kWh) | 0.57689 | 0.61 - IESS coal and gas power stations GoI | [8 empty] | scenario_battery (blank for base) | base | base | base | base | base
Coal (kcal/kWh) | 2375 | CERC 2014 "Recommendations on Operation Norms for Thermal Power Stations Tariff Period 2014-19" | [8 empty] | disc_rate | 7% | 7% | 7% | 7% | 7%
[11 empty] | crf | 0.085811 | 0.085811 | 0.085811 | 0.085811 | 0.085811
NG (INR/GJ) | 240 | [9 empty] | CT
NG (USD/GJ) | 3.6923 | [8 empty] | USD/kW | cap_cost_ct | 678.2677 | 678.2677 | 678.2677 | 678.2677 | 678.2677
LNG (USD/MMBTU) | 10 | [8 empty] | USD/GJ | gas_price | 10 | 10 | 10 | 10 | 10
LNG (USD/GJ) | 9.4787 | [9 empty] | Annualized fixed costs (USD/kW-y) | 65.0025 | 65.0025 | 65.0025 | 65.0025 | 65.0025
NG heat rate - CT (kcal/kWh) | 3065 | CERC 2014 average | [8 empty] | Variable cost (USD/MWh) | 126.9742 | 126.9742 | 126.9742 | 126.9742 | 126.9742
NG heat rate - CCGT (kcal/kWh) | 2071 | CERC 2014 average
NG heat rate - CT (kcal/kWh) | 2900 | NEP 2016 | [8 empty] | CCGT
NG heat rate - CCGT (kcal/kWh) | 2000 | NEP 2016 | [7 empty] | USD/kW | cap_cost_ccgt | 775.1631 | 775.1631 | 775.1631 | 775.1631 | 775.1631
NG heat rate - coal super critical (kcal/kWh) | 2250 | NEP 2016 | [8 empty] | Annualized fixed costs (USD/kW-y) | 77.5171 | 77.5171 | 77.5171 | 77.5171 | 77.5171
NG heat rate - CT (Btu/kWh) | 10390 | B&V average | [8 empty] | Variable cost (USD/MWh) | 84.9368 | 84.9368 | 84.9368 | 84.9368 | 84.9368
NG heat rate - CCGT (Btu/kWh) | 6705 | B&V average
Coal
source: http://cercind.gov.in/2014/regulation/reg21.pdf | [9 empty] | USD/kW | cap_cost_coal | 976.4278 | 3233.3116 | 976.4278 | 976.4278 | 976.4278
source: B&V 2012 | [9 empty] | USD/GJ | fuel_cost_coal | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154
| CT | CCGT | Coal | source |  |  | CT | CCGT | Coal |  | Annualized fixed costs (USD/kW-y) | 125.8878 | 319.5521 | 125.8878 | 125.8878 | 125.8878
Capital cost (USD/kW) | 678.2677 | 775.1631 | 976.4278 |  |  | Capital cost (INR/kW) | 44087.4 | 50385.6 | 63467.8098 |  | Variable cost (USD/MWh) | 32.4666 | 32.4666 | 32.4666 | 32.4666 | 32.4666
Fixed O&M (USD/kW-y) | 6.8 | 11 | 42.1 |  |  | Fixed O&M (INR/kW-y) | 442 | 715 | 2736.5
Variable O&M (USD/MWh) | 10.7 | 3.5 | 4.6 |  |  | Variable O&M (INR/MWh) | 695.5 | 227.5 | 299 |  | Crossover points
Heat Rate (Btu/kWh) | 11500.443 | 7931.34 | 8922.7575 | B&V & CERC 2014 operating norms | See NEP Vol I page 151 for more estimates |  |  |  |  | parameter | gas_ct | 0.033984 | 0.033984 | 0.033984 | 0.033984 | 0.033984
Heat Rate (kcal/kWh) (converted from Btu/kWh) | 2900 | 2000 | 2250 | B&V | CERC 2014 heat rate for super critical is 2375; NEP Vol I for coal is 2350; gas is 1850 (doesn't say which gas). | [5 empty] | gas_ccgt | 0.10524 | 0.52658 | 0.10524 | 0.10524 | 0.10524
Heat Rate (MJ/kWh) converted from Btu/kWh) | 12.133 | 8.3676 | 9.4135 | [7 empty] | coal | 1 | 1 | 1 | 1 | 1
Minimum load | 50% | 50% | 55% | CERC
Emissions CO2 (lbs/mmbtu) | 117 | 117 | 215 | B&V | [6 empty] | Screening Curves
Emissions SO2 (lbs/mmbtu) | 0.0002 | 0.0002 | 0.055 | B&V | [5 empty] | hour | technology
Emissions Nox (lbs/mmbtu) | 0.033 | 0.0073 | 0.05 | B&V |  | 807.6923 |  |  |  | 0 | CT-LNG | 65.0025 | 65.0025 | 65.0025 | 65.0025 | 65.0025
PM10 (lbs/mmbtu) | 0.006 | 0.0058 | 0.011 | B&V |  | 551.6923 |  |  |  | 8760 | CT-LNG | 1177.2962 | 1177.2962 | 1177.2962 | 1177.2962 | 1177.2962
Emissions CO2 (tonnes/MWh) | 0.61161 | 0.4218 | 0.872 |  | See NEP Vol I page 241; page 309 shows gas as 0.49, coal as 1.01 |  |  |  |  | 0 | CCGT-LNG | 77.5171 | 77.5171 | 77.5171 | 77.5171 | 77.5171
Emissions SO2 (kg/MWh) | 0.0010455 | 0.00072103 | 0.22307 | [6 empty] | 8760 | CCGT-LNG | 821.5637 | 821.5637 | 821.5637 | 821.5637 | 821.5637
Emissions Nox (kg/MWh) | 0.17251 | 0.026318 | 0.20279 | [6 empty] | 0 | Coal | 125.8878 | 319.5521 | 125.8878 | 125.8878 | 125.8878
PM10 (kg/MWh) | 0.031365 | 0.02091 | 0.044614 | [6 empty] | 8760 | Coal | 410.2953 | 603.9596 | 410.2953 | 410.2953 | 410.2953
Auxillary consumption | 1% | 2.5% | 10% | CERC 2014 Operating norms for gas
[10 empty] | Only fixed costs USD/kW-y | generator_cost_all
Discount rate | 7% | 7% | 7% | CERC - 10.8% is probably nominal, so using 7% | [5 empty] | cost_type | technology
Plant life | 25 | 25 | 25 | CERC 2014 | [5 empty] | capital | ct | 678.2677 | 678.2677 | 678.2677 | 678.2677 | 678.2677
CRF | 0.085811 | 0.085811 | 0.085811 | [6 empty] | om | ct | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
Annualized fixed costs (USD/kW-y) | 65.0025 | 77.5171 | 125.8878 | [6 empty] | capital | ccgt | 775.1631 | 775.1631 | 775.1631 | 775.1631 | 775.1631
Annualized fixed costs (INR/kW-y) | 4225.1626 | 5038.6144 | 8182.7056 |  |  | Expected PLF in hours | 297.7029 | 624.1655 | 7540.4286 | om | ccgt | 11 | 11 | 11 | 11 | 11
Variable cost (USD/MWh) | 126.9742 | 84.9368 | 32.4666 |  |  |  | CT | CCGT | Coal | capital | coal | 976.4278 | 3233.3116 | 976.4278 | 976.4278 | 976.4278
Variable cost (INR/MWh) | 8253.3212 | 5520.8933 | 2110.3295 |  |  | Fixed cost INR per kWh | 14.1925 | 8.0726 | 1.0852 | om | coal | 42.1 | 42.1 | 42.1 | 42.1 | 42.1
Crossover points | 3.398% | 10.52% |  |  |  | Total cost INR per kWh | 22.4459 | 13.5935 | 3.1955 | capital | wind | 1100 | 1100 | 770 | 1100 | 770
Crossover points - only CT and coal | 7.354% | [8 empty] | om | wind | 15 | 15 | 15 | 15 | 15
[10 empty] | capital | solarPV | 900 | 900 | 900 | 630 | 630
[10 empty] | om | solarPV | 10 | 10 | 10 | 10 | 10
For screening curve plots | [9 empty] | capital | battery | 0 | 0 | 0 | 0 | 0
Hour | [9 empty] | om | battery | 0 | 0 | 0 | 0 | 0
0 | 65.0025 | 77.5171 | 125.8878
8760 | 1177.2962 | 821.5637 | 410.2953
Cutoff Hour | 297.7029 | 921.8685 | 0
Note on B6: Ranjit: http://cornerstonemag.net/coal-based-electricity-generation-in-india/
Note on A8: Ranjit: Sub-bituminous http://www.industry.gov.au/Office-of-the-Chief-Economist/Publications/Documents/Coal-in-India.pdf
Note on B16: Ranjit: http://cornerstonemag.net/coal-based-electricity-generation-in-india/
Note on B18: Ranjit: multiple sources. See Data and Sources Worksheet.
Note on D34: Ranjit: This B&V number matched CERC 2014 numbers
Note on B37: Ranjit: Key difference between CT vs CCGT/coal is that it can start stop during the day.
Note on D37: Ranjit: India's regulation. B&V 's was 40%.

## CF_crossover_points
parameter | coallc | coalhc | coallcW30lc | coallcS30lc | coallcW30lcS30lc
gas_ct | 0.033984 | 0.033984 | 0.033984 | 0.033984 | 0.033984
gas_ccgt | 0.10524 | 0.52658 | 0.10524 | 0.10524 | 0.10524
coal | 1 | 1 | 1 | 1 | 1
gas_price | 10 | 10 | 10 | 10 | 10
cap_cost_ct | 678.2677 | 678.2677 | 678.2677 | 678.2677 | 678.2677
cap_cost_ccgt | 775.1631 | 775.1631 | 775.1631 | 775.1631 | 775.1631
cap_cost_coal | 976.4278 | 3233.3116 | 976.4278 | 976.4278 | 976.4278

## screening_curve_plot
hour | technology | coallc | coalhc
0 | CT-LNG | 65.0025 | 65.0025
8760 | CT-LNG | 1177.2962 | 1177.2962
0 | CCGT-LNG | 77.5171 | 77.5171
8760 | CCGT-LNG | 821.5637 | 821.5637
0 | Coal | 125.8878 | 319.5521
8760 | Coal | 410.2953 | 603.9596

## generator_cost_all
cost_type | technology | coallc | coalhc | coallcW30lc | coallcS30lc | coallcW30lcS30lc
capital | ct | 678.2677 | 678.2677 | 678.2677 | 678.2677 | 678.2677
om | ct | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
capital | ccgt | 775.1631 | 775.1631 | 775.1631 | 775.1631 | 775.1631
om | ccgt | 11 | 11 | 11 | 11 | 11
capital | coal | 976.4278 | 3233.3116 | 976.4278 | 976.4278 | 976.4278
om | coal | 42.1 | 42.1 | 42.1 | 42.1 | 42.1
capital | wind | 1100 | 1100 | 770 | 1100 | 770
om | wind | 15 | 15 | 15 | 15 | 15
capital | solarPV | 900 | 900 | 900 | 630 | 630
om | solarPV | 10 | 10 | 10 | 10 | 10
capital | battery | 0 | 0 | 0 | 0 | 0
om | battery | 0 | 0 | 0 | 0 | 0

## Data and sources
Data and sources
| CT | CCGT | Coal SC | Coal SubC | Nuclear | Hydro | Sources
Capital costs
USD/kW (2015 $) | 678 | 978 | 3636 |  | 5945 |  | EIA Capital cost estimates for utility scale elec gen plants 2016; coal cost is only for ultra-supercritical; CT is advanced (regular one is 1101)
USD/kW (2016 $) | 686.5428 | 990.3228 | 3681.8136 |  | 6019.907 |  | EIA 2016 adjusted for inflation
USD/kW (2009$) | 651 | 1230 | 2890 |  | 6100 | 3500 | B&V-NREL 2012; coal is pulverized coal plant
USD/kW (2016 $) | 728.3342 | 1376.1153 | 3233.3116 |  | 6824.637 | 3915.7753 | B&V-NREL 2012; adjusted for inflation
INR Rs lakhs/MW (2012) | 358.7 | 358.7 | 525 | 475 |  |  | IESS 2047; gas costs are not split into CCGT and CT. don't use
INR Rs lakhs/MW (2016) | 470.3699 | 470.3699 | 688.4422 | 622.8762 |  |  | IESS 2047 adjusted for inflation
USD/kW (2016 USD) | 723.646 | 723.646 | 1059.1418 | 958.2711 |  |  | IESS 2047; first apply inflation rate and then convert to USD
INR Rs lakhs/MW (2015) | 420 | 480 | 537 | 508 |  |  | Phadke et al 2016
INR Rs lakhs/MW (2016) | 440.874 | 503.856 | 563.6889 | 533.2476 |  |  | Phadke et al 2016 adjusted for inflation
USD/kW (2016) | 678.2677 | 775.1631 | 867.2137 | 820.3809 |  |  | Phadke et al 2016
INR Rs lakhs/MW (2012) |  |  | 484 | 468 |  |  | CERC 2012 Benchmark capital costs for thermal power stations with coal as fuel; average of costs of six units of 660 MW for SC and another six units of 500 MW for SubC
INR Rs lakhs/MW (2016) |  |  | 634.6781 | 613.697 |  |  | CERC 2012 adjusted for inflation
USD/kW (2016) |  |  | 976.4278 | 944.1492 |  |  | CERC 2012 adjusted for inflation
O&M
O&M (INR/kW-y)(2016) | 3813 | 1657 | 1627 | 1808 |  |  | CERC (Terms and Conditions of Tariff) Regulations 2014; values are for 2016-17, so no inflation rate applied
O&M (USD/kW-y)(2016) | 58.6615 | 25.4923 | 25.0308 | 27.8154 |  |  | CERC (Terms and Conditions of Tariff) Regulations 2014 - not sure if these include variable O&M as well. I am assuming not. Then gas O&M make sense, but coal for India is much lower than US, which also makes sense.
O&M (INR/MWh) (2016) | 0 | 0 | 0 | 0 |  |  | CERC 2014 assumed zero
O&M (USD/MWh) (2016) | 0 | 0 | 0 | 0 |  |  | CERC 2014 assumed zero
O&M (USD/kW-y) | 6.8 | 11 | 42.1 |  | 5945 |  | EIA 2016 (combine with variable)
O&M (USD/MWh) | 10.7 | 3.5 | 4.6 |  |  |  | EIA 2016 (combine with fixed)
O&M (USD/kW-y) (2009$) | 5.26 | 6.31 | 23 |  | 127 | 15 | B&V (combine with variable)
O&M (USD/MWh) (2009$) | 29.9 | 3.67 | 3.71 |  | 0 | 6 | B&V (combine with fixed)
O&M (USD/kW-y) (2016$) | 5.8849 | 7.0596 | 25.7322 |  | 142.0867 | 16.7819 | B&V (combine with variable)
O&M (USD/MWh) (2016$) | 33.4519 | 4.106 | 4.1507 |  | 0 | 6.7128 | B&V (combine with fixed)
Heat rates
kcal/kWh |  |  |  | 2375 |  |  | CERC (Terms and Conditions of Tariff) Regulations 2014
kcal/kWh | 3065 | 2071 |  |  |  |  | CERC Operating norms for thermal power generating plants 2014; Average of plants mentioned in order
kcal/kWh | 2900 | 2000 | 2250 | 2365 |  |  | National Electricity Plan Draft - CEA 2016; page 152 coal 660 MW unit
Btu/kWh | 9800 | 6600 | 8800 |  |  |  | EIA 2016
kcal/kWh (converted) | 2471.2092 | 1664.2837 | 2219.045 |  |  |  | EIA 2016
Btu/kWh | 10390 | 6705 | 9370 |  | 9720 |  | B&V-NREL 2012
kcal/kWh (converted) | 2619.986 | 1690.761 | 2362.7785 |  |  |  | B&V-NREL 2012
Aux consumption
Discount rates
% | 6.25% | Central bank December 2016
| 10.8% | CERC regulations (I think this is nominal discount rate because it determines tariff over the lifetime of the plant)
LNG
USD/MMBTU | 10.7 | 12.7 - Indonesian LNG in Japan - source IMF (2016) - Quarterly average from 2014 Q1 to 2016 Q2 ; 10.7 - Indonesian LNG in Japan - IMF - average of medium term commodity baseline that includes past baseline data from 2009 to 2016, and future projections till 2021
| 8.5 | IMF (2017) LNG forecast for 2017-2022 Indonesian gas in Japan
| 10 | World Bank forecast (2017) for 2030 for Natural Gas LNG in Japan
| 5.5 | World LNG Estimated Landed Prices June 2017 - Federal Energy Regulatory Commission (2017)
(FERC - 5.57 landed in India - https://www.ferc.gov/market-oversight/mkt-gas/overview/ngas-ovr-lng-wld-pr-est.pdf)
Outage rates
Solar and wind costs | Wind | Solar PV
1USD to Rs | 65 | 65
Capital cost adjusted (USD/kW) | 1100 | 900
Capital cost adjusted (INR/kW) | 71500 | 58500
Discount rate | 7% | 7%
Plant Life (years) | 25 | 25
CRF | 0.085811 | 0.085811
Fixed O&M Costs (USD/kW) | 15 | 10
Variable O&M Costs (USD/kWh) | 0 | 0
Average capacity factor | 25% | 19.7% | These are average capacity factors from S0W400 and S400W0 generation profiles
LCOE (USD/MWh) | 49.9505 | 50.5467
LCOE (INR/kWh) | 3.2468 | 3.2855
Note on B20: Ranjit: CERC 2014 page 74, Small gas turbine power gen 2016-17 costs
Note on C20: Ranjit: CERC 2014 page 74, CCGT 2016-17
Note on D20: Ranjit: CERC 2014 for 2016-17 for supercritical 600 MW coal
Note on E20: Ranjit: page 72 500 MW subcritical coal. 2016-17 costs
Note on E32: Ranjit: page 103; 500 MW plant
Note on B59: Ranjit: US wind installed cost in 2015 - $1690/kW - Wind report 2015 market data

## inflation rate
India Inflation rates
source: Consumer Price Index India
http://www.inflation.eu/inflation-rates/india/historic-inflation/cpi-inflation-india.aspx
INDIA
Cumulative inflation factors
| Average annual inflation rate | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
2008 | 8.32% | bar: 2008
2009 | 10.83% | 2008: 1.1083; 2009: 1
2010 | 12.11% | 2008: 1.2425; 2009: 1.1211; 2010: 1
2011 | 8.87% | 2008: 1.3527; 2009: 1.2205; 2010: 1.0887; 2011: 1
2012 | 9.3% | 2008: 1.4785; 2009: 1.3341; 2010: 1.1899; 2011: 1.093; 2012: 1
2013 | 10.92% | 1.64 | 1.4797 | 1.3199 | 1.2124 | 1.1092 | 1
2014 | 6.37% | 1.7445 | 1.574 | 1.404 | 1.2896 | 1.1799 | 1.0637 | 1
2015 | 5.88% | 1.847 | 1.6665 | 1.4865 | 1.3654 | 1.2492 | 1.1262 | 1.0588 | 1
2016 | 4.97% | 1.9388 | 1.7494 | 1.5604 | 1.4333 | 1.3113 | 1.1822 | 1.1114 | 1.0497 | 1
2017 | 2.08% | 1.9792 | 1.7858 | 1.5929 | 1.4631 | 1.3386 | 1.2068 | 1.1345 | 1.0715 | 1.0208 | 1
US
Cumulative inflation factors
| Average annual inflation rate | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
2008 | 3.85% | bar: 2008
2009 | -0.34% | 2008: 0.9966; 2009: 1
2010 | 1.64% | 2008: 1.0129; 2009: 1.0164; 2010: 1
2011 | 3.16% | 2008: 1.045; 2009: 1.0485; 2010: 1.0316; 2011: 1
2012 | 2.07% | 2008: 1.0666; 2009: 1.0702; 2010: 1.053; 2011: 1.0207; 2012: 1
2013 | 1.47% | 1.0823 | 1.086 | 1.0684 | 1.0357 | 1.0147 | 1
2014 | 1.62% | 1.0998 | 1.1035 | 1.0857 | 1.0525 | 1.0311 | 1.0162 | 1
2015 | 0.12% | 1.1011 | 1.1049 | 1.087 | 1.0537 | 1.0324 | 1.0174 | 1.0012 | 1
2016 | 1.26% | 1.115 | 1.1188 | 1.1007 | 1.067 | 1.0454 | 1.0302 | 1.0138 | 1.0126 | 1
2017 | 2.22% | 1.1397 | 1.1436 | 1.1252 | 1.0907 | 1.0686 | 1.0531 | 1.0363 | 1.0351 | 1.0222 | 1

## scenarios
Scenarios and sensitivities
Scenarios | VRE Buildout Capacity | VRE Buildout share | Capacity expansion | System operations | Exogenous to models | scenario abbreviation | method | comment
Base | 0 | S0 - W0
| 200 | S0 - W100
| 200 | S25 - W75
| 200 | S50 - W50
| 200 | S75 - W25
| 200 | S100 - W0
| 300 | S0 - W100
| 300 | S25 - W75
| 300 | S50 - W50
| 300 | S75 - W25
| 300 | S100 - W0
| 400 | S0 - W100
| 400 | S25 - W75
| 400 | S50 - W50
| 400 | S75 - W25
| 400 | S100 - W0
Sensitivities
Base case |  |  | Discount rate 7%, Min gen level 70%
|  |  | Low Cost Coal |  |  | coalLC
|  |  | High Cost Coal |  |  | coalHC | screening curve | add FGD and other adders from CEA report
|  |  |  | Minimum gen level 55% |  | 55min | econ dispatch script
[5 empty] | Solar lower costs 10% | solarLC10p | R script
[5 empty] | Solar lower costs 20% | solarLC20p | R script
[5 empty] | Wind lower costs 10% | windLC10p | R script
[5 empty] | Wind lower costs 20% | windLC20p | R script
|  |  | Hydro 25% lower |  |  | hydroHE25p | input file with extension | high energy
|  |  | Hydro 25% higher |  |  | hydroLE25p | input file with extension | low energy
|  |  | Nuclear 64 GW |  |  | nuc64 |  | I don't have capacity costs for nuclear. Can only determine energy value
|  |  | Battery Storage 5% peak ~ 15 GW |  |  | stoBat15 | input file with extension | maybe
|  |  | Battery Storage 10% peak ~ 30 GW |  |  | stoBat30 | input file with extension | that's 15% of solar 200 GW target
|  |  | Battery Storage 15% peak ~ 45 GW |  |  | stoBat45 | input file with extension | maybe
|  |  | Battery Storage 20% peak ~ 60 GW |  |  | stoBat60 | input file with extension | that's 30% of solar 200 GW target
|  |  | Demand response 5% daily energy |  |  |  |  | CANCEL; just compare DR to storage in text. Storage efficiency, which leads to additional energy for charging is akin to DR rebound whre consumption may increase in non-peak hours.
|  |  | Demand response 10% daily energy |  |  |  |  | CANCEL; just compare DR to storage in text. Storage efficiency, which leads to additional energy for charging is akin to DR rebound whre consumption may increase in non-peak hours.
|  |  | Discount rate 4% |  | Discount rate 4% VRE costs |  |  | CANCEL?
|  |  | Discount rate 10% |  | Discount rate 10% VRE costs |  |  | CANCEL?
|  |  | Load shape change |  |  | loadMod2014
|  |  | 2012 load |  |  |  |  | maybe
|  |  | 2013 load |  |  |  |  | maybe
|  |  | Wind 100m HH |  |  | wind100
|  |  | Wind 120m HH |  |  | wind120
|  |  | Solar 1axis tracking |  |  | solar1A
|  |  | Solar 45deg Southwest |  |  | solar45deg
|  |  | Solar 90deg West |  |  | solar90deg
|  |  | net load script | screening curve script | econ dispatch script | cost summary R script
|  |  | wind80/100/120 | coalLC/HC | 70min/55min | solarLC10p/20p/30p
|  |  | solar0/45/90/1A | gasLC/HC |  | windLC10p/20p/30p
hydro0/HE25/LE25
nuc0/64
loadMod
stoBat30/60
|  |  | Cost | Capacity value | Energy value
|  |  | solarLC10p/20p/30p | wind80/100/120 | wind80/100/120
|  |  | windLC10p/20p/30p | solar0/45/90/1A | solar0/45/90/1A
|  |  | stoBat30/60 | hydro0/HE25/LE25 | hydro0/HE25/LE25
|  |  |  | nuc0/64 | nuc0/64
|  |  |  | loadMod | loadMod
|  |  |  | stoBat30/60 | stoBat30/60
|  |  |  | coalLC/HC | coalLC/HC
|  |  |  | gasLC/HC | gasLC/HC
70min/55min

## run_times
Simulations |  |  | econ dispatch script |  |  | econ dispatch net load script
run |  |  | minutes | hours | estimated time for 16 mixes and targets | mins
S200W00 | battery30 | lookahead | 216 | 3.6 | 54 | 3
S200W00 | battery30 | nolookahead | 88 | 1.4667 | 22 | 3
S200W00 | no battery |  |  | 0 | 0 | 3
S200W00 | no battery | nolookahead | 89 | 1.4833 | 22.25 | 3